三季度抵美船舶检查重点

PSC focus for ships arriving in the United States in the third quarter

检查重点是应急发电机的检查和试验，具体检查项目如下:

The focus is the inspection and testing of Emergency Generator, the specific inspection items are as follows:

- 高压燃油输送管线无泄漏或修复不当;

No leakage or improper repair of the high-pressure fuel supply pipeline.

- 冷却管线无泄漏或不当修复;

No leakage or improper repair of cooling pipelines.

- 高压管路双层夹套;

Double-layer jacket for high-pressure pipelines.

- 旋转机械周围有防护装置;

There are protective devices around the rotating parts.

- 保温层牢固安装且未被油浸湿;

The insulation layer is firmly installed and not soaked with oil.

- 过度泄漏或不当修复;

Excessive leakage or improper repair.

- 发动机过度抖动/喘振(转速差异);

Excessive engine jitter/surge (speed difference).

- 设置为自动启动;

Set to start automatically.

- 带负载运行的定期测试记录;

Regular test records for load operation.

- 应急发电机具有独立的燃料供应;

The specific fuel supply of E/G.

- 超过500升的燃油箱在空间外有紧急关闭阀;

The fuel tank with over 500 liters has an emergency shut-off valve outside the space

- 向电气配电板提供足够的电压/频率(60赫兹);

Provide sufficient voltage/frequency to the electrical distribution board (60 Hz)

- 开关柜前的非导电垫;

Non-conductive pads in front of the switch cabinet

- 抽查轮机日志对E/G故障记录;

Random check the E/G fault record in E/R log book.

- 使用两个独立的启动源启动发动机;

Start the engine using two independent start sources respectively.